| دفتر الشروط الفني لتوريد, و تركيب و تشغيل مرجل بخاري ضغط 38kg/cm² في الشركة العامة لمصفاة حمص (على أساس مفتاح باليد) المحتويات : - الموضوع. - القسم الميكانيكي. - القسم الكهربائي. - قسم الأجهزة الدقيقة . - القسم المدني . - قسم معالجة المياه . - متطلبات عامة. - المرفقات . 1- الموضوع : يهدف هذا العمل إلى تصميم و توريد وتركيب وتشغيل مرجل بخاري , المشروع ( على أساس مفتاح باليد) . يقدم المشروع إلى الشركة العامة لمصفاة حمص بضمان شروط التشغيل . وفق المواصفات الفنية التالية : - ضغط البخار الخارج : 38 كغ/سم2. - حرارة البخار الخارج : 450 ± 5 درجة مئوية. - كمية البخار الخارج: 25طن/ ساعة على الأقل - عدد حرا قات المرجل: حراقين . 2- القسم الميكانيكي 2-1- مواصفات المرجل : - ضغط البخار الخارج : 38 كغ/سم2. - حرارة البخار الخارج : 450 ±5 درجة مئوية. - كمية البخار الخارج : 25طن / ساعة على الأقل . - مواصفات المياه والوقود المقدمة من المصفاة - حرارة مياه التغذية : درجة حرارة الجو (5-20 ) درجة مئوية. - نوع مياه تغذية المرجل : مياه ديمي ( معالجة ) مرفق مواصفات المياه . - ضغط مياه التغذية : الضغط الجوي النظامي . - الوقود المستخدم في حرق المرجل : - فيول أويل (مرفق مواصفاته ) بضغط جوي نظامي وحرارة ( 70-80 ) م° الى حدود المرجل . - فيول غاز (مرفق مواصفاته ) بضغط (3.5 - 4 ) كغ/سم2 . 2-2- متطلبات فنية : - يجب أن يكون المرجل قادرا على إنتاج البخار بضغط وحرارة وكمية التدفق المطلوبة عند حرق أي نوع من أنواع الفيول المحددة . - يجب أن يبقى الضغط التشغيلي ودرجة حرارة البخار ثابتين عند أي حمولة للمرجل ابتداءً من 60%. - يجب ألا يقل المردود عن 91% عند الحمولة الاسمية . - على العارض تقديم مخططات استهلاك الوقود ( الفيول والغاز ) للمرجل . - يجب أن يذكر العارض أنواع المعادن لكافة الأنابيب المستعملة في المرجل ومواصفاتها الفيزيائية والكيميائية والميكانيكية وفق الستاندرات ذات الصلة . - على العارض تقديم مجموعتي ضخ لتغذية المرجل بمياه التغذية مع الملحقات اللازمة لعملهما , واحدة في التشغيل والأخرى احتياط . - يجب أن تكون الحراقات المسلمة وفق أحدث الأنواع ذات الإصدارات NOx المنخفضة ويجب أن تكون قادرة على الحرق التام , النظيف والفعال لجميع أنواع الوقود المذكورة أنفا . - تقديم محولة ضغط 38/14bar ذات تحكم آلي مع تجهيزاتها . - يجب أن تركب مدخنة مستقلة للمرجل تحقق الشروط التشغيلية و البيئية . - يجب على المتعاقد تركيب صمامات مناسبة على جميع الخطوط بحيث تسمح بعزل المرجل عن كافة خطوط الدخل والخرج . - يجب على المتعاقد تركيب سلالم , أدراج , منصات وممرات مشاة مغلفنة لتأمين وصول كامل لجميع الأجهزة والمعدات بسهولة . - يجب أن يكون المرجل محمي بواقية مناسبة . - يجب أن تكون جميع المواد والمعدات جديدة وليست مجددة , - يمكن للعارض القيام بزيارة للمصفاة لكي يطلع بشكل كامل على موقع تركيب المرجل . 2-3- العزل : - يجب أن تعزل جميع السطوح التي تزيد درجة حرارتها عن 60 درجة مئوية أينما وجدت . يجب أن يعزل المرجل والأوعية والأنابيب باستخدام مادة (صديقة للبيئة) وأن تحمى هذه المادة بصفائح من الألمونيوم . - يجب أن تجهز علب عزل سهلة الفك في جميع المواقع التي قد تحتاج الى فك بهدف الإصلاح 3- القسم الكهربائي المتطلبات الكهربائية : 1-جميع التجهيزات الكهربائية الخاصة بالمرجل يجب أن تكون مناسبة من حيث التصنيف الحراري والغازي والتي يعمل عليها المرجل . 2 - التجهيزات الكهربائية التي ستقدم للمرجل يجب أن تخضع لأحدى الستندرات العالمية : . أو مايعادلها ( NEC- IEC) 3- نظام التغذية الكهربائية المستخدم : 380/220 فولت 50 هرتز – 3فاز +نتر + حيادي -400 فولت- مقبول . 4- تقديم جميع المخططات التوضيحية والنشرات الفنية للتجهيزات التي ستركب ودارات التشغيل . 5- تقديم شهادة اختبار ضد الانفجار للمحركات ذات التصنيف الانفجاري والتجهيزات ذات الصلة 6- تقدم المصفاة التغذية الكهربائية الضرورية للوحة تشغيل المرجل . 4-قسم الأجهزة الدقيقة-4-1- الأجهزة الحقلية : - وتشمل (المبينات الموقعية والمفاتيح و المرسلات) لبارامترات العمل (الضغط والمستوى والحرارة و والكمية والتدفق ) - يجب أن تكون جميع الأجهزة الحقلية حديثة وذات درجة حماية IP67 وأن تكون متوافقة من حيث التصنيع والتركيب مع الستاندرات الأوربية الحديثة أو ما يكافئها . - تغذية جميع الأجهزة الحقلية 24 V DC . 4-2– نظام التحكم الآلي بالمرجل : يجب أن يكون النظام المقدم من نوع التحكم المنطقي القابل للبرمجة ( PLC ) مؤلفاً كحد أدنى من حلقات التحكم الرئيسية التالية : - نظام التحكم بالحرق . - حلقة التحكم بمياه التغذية . - حلقة التحكم بدرجة حرارة البخار . - نظام قيادة الحراقات . - تركيب علبة تحكم محلية للحراقات المستخدمة وذات درجة حماية IP55 على الأقل . - يجب أن تكون مكونات نظام التحكم المقدم اصدار حديث مخصص للاستخدام في مجال التحكم بالمراجل البخارية . - يجب تركيب واجهة تخاطب (HMI) . - يجب توفر إمكانية للتشغيل والإقلاع والفصل الطارئ من الموقع بالإضافة إلى واجهة التخاطب . - يجب أن تكون الواجهة ذات شاشة تؤمن الإظهار والاستعراض بالزمن الحقيقي و الأرشيف . وعرض الحمايات و الإنذارات - توضع مجموعة PLC في خزانة مناسبة وتتصل مع HMI . ويتوجب على المتعهد تأمين غرفة مناسبة لوضع الخزانة تتيح العمل عليها بشكل سهل ومريح . - على المتعاقد تركيب كل ما يلزم للتشغيل والفصل الصحيح والأمن وفقا لتصميمه ( ريليات , لمبات , قواطع , زمور , .. ) حتى لو لم تذكر أعلاه . 4-5- ملحقات النظام : - حاسب محمول حديث لتحميل برمجيات التحكم . - طابعة ليزرية ملونة لطباعة التقارير . 4-6- كابلات الوصل : - على المتعهد تقديم كابلات ( مسلحة وذات عازل PVC وغمد نحاسي وأن تكون مقاومة للحرارات العالية ) - يجب وضع الكابلات داخل مجاري معدنية وعلى حوامل مناسبة للموقع . - بقاء 25 % من سعة الكابلات كاحتياط . 5- القسم المدني 5-1 معلومات الموقع : وصف الموقع: المشروع يقع ضمن شركة مصفاة حمص التي تقع على ارتفاع 495 م عن سطح البحر . معلومات التربة : على المتعاقد إجراء كل الاختبارات اللازمة على التربة لأهداف تصميمية . 5-2 الحفر والردم : - على المتعاقد أن ينفذ أعمال الحفر ( الطرق والقنوات و القنوات الكهربائية والأساسات و الخ ..) ويردم مناطق الحفر بتربة مناسبة على طبقات مرصوصة جيداً . - يجب أن توضع الكابلات الكهربائية في قنوات بيتونية ثم تملأ هذه القنوات بالرمل وتلون بالأحمر . 5-3- تصريف المرجل والتصريف العام للموقع : التزام العارض تقديم تصميم لنظام التصريف في المرجل وكذلك تصريف كامل موقع العمل وربط هذا النظام بشبكة الصرف الصحي في المصفاة . 5-4- الدهان : على العارض أن يبين في عرضه الدهان المستخدم لطلاء الأنابيب ,الهيكل المعدني ,المعدات الميكانيكية ,الخ .. 5-5- التصميم الزلزالي : الدرجة VII وفقاً للستاندرات : (MSK SCALE,MERCALLI). 5-6 نظام إنذار حريق : -يجب على المتعاقد أن يؤمن ويركب نظام إنذار حريق وجميع دارات إنذار الحريق الضرورية في موقع المشروع ويربط النظام مع نظام إنذار الحريق في المصفاة . 6- قسم معالجة المياه 6-1- مواصفات المياه المستخدمة : - درجة الحموضة = ( PH = 7±1 ) . - الناقلية ( 25°م ) = 0.5 ميكروسيمنس/ سم . - محتوى السيليكا = 20 ميكرو غرام / لتر . -درجة الحرارة = درجة الحرارة الجو المحيطة 6-2- نظام المعالجة الكيميائية الداخلية للمرجل - يجب على العارض تقديم نظام الحماية الكيميائية اللازمة لدارة المرجل مع كافة المعدات اللازمة لذلك من مضخات وخزانات وملحقاتها , وكذلك تقديم المواد الكيميائية المستخدمة لهذه الغاية خلال سنة الضمان , وأن يضمن تشغيلها بشكل جيد وآمن , وتركب على ارتفاع صفر متر . وكل ما ذكر سابقا حسب الستندرات العالمية . 6-3- العينات : - على العارض تقديم تجهيزات العينات الضرورية مع الأجهزة المخبرية اللازمة لإجراء تحاليل العينات( جهاز سبكترو فوتوميتر , جهاز قياس ناقلية , جهاز قياس PH ) على الاقل . وأن تكون هذه التجهيزات وفق الستندرات العالمية - يجب على العارض تقديم طريقة تحليل العينات وفق الستاندرات العالمي. 6-4- الغسيل الكيميائي للمرجل : - على العارض أن يقدم الكيميائيات الضرورية ( كمية ونوعية ) التي سوف تستخدم في غسيل المرجل والوثائق الفنية ذات الصلة . - على العارض تقديم برنامج غسيل المرجل كيميائيا الذي يجب أن يكون حسب الستندرات العالمية ذات الصلة . على المتعاقد إجراء عملية الغسيل الكيميائية . 7- متطلبات عامة 7-1- عموميات : - يجب أن يصمم المرجل , يركب ويفحص للقبول وفق أحدث نسخ من الستندارات ذات الصلة . " مرفق جدول بالستندرات المطلوبة " - يجب على المتعاقد ترميز جميع الخطوط والمعدات .بالاضافة الى ترقيم عناصر دارات القياس والتحكم بما يطابق مخططات المشروع - على المتعاقد ربط خطوطه مع خطوط المصفاة ( مياه, وقود , هواء , بخار.. .) - يجب على المتعاقد تقديم جدول زمني لتنفيذ الأعمال . - أي ضرر ناتج عن أعمال المتعهد أو متعهد ثانوي من جانبه لأي قسم من التركيبات الكائنة في المصفاة مثل الطرق , خطوط الكهرباء , المياه , أنابيب البخار... الخ سوف تقع على مسؤولية المتعاقد . - على المتعاقد مراعاة قواعد الأمن والسلامة المتبعة في المصفاة خلال فترة التنفيذ . - يجب أن تنجز اختبارات الأداء والتشغيل للمرجل المقدّم خلال فترة أسبوع واحد من أجل إثبات الضمانات . - يجب على المتعاقد تقديم شهادة اختبار لجميع التجهيزات باللغة الانكليزية . - على العارض تقديم قائمة تحليل أسعار لكافة أعمال المرجل ( توريد , تركيب , تشغيل ) في عرضه المالي . 7-2- قطع الغيار : - على العارض تقديم قوائم بقطع الغيار لخمسة سنوات تشغيلية واحدة غير مسعرة ضمن عرضه الفني وأخرى مسعرة ضمن عرضه المالي , تحتفظ شركة مصفاة حمص بحق اختيار ما تراه مناسبا من هذه القوائم أثناء الدراسة الفنية . على أن تتضمن قائمة قطع الغيار على الأقل مايلي: بالنسبة لقسم الأجهزة الدقيقة : - المكونات الأساسية لآلية إقلاع الحراق ( مراقب لهب , شمعات اشتعال , .... ) - 10% من طول الكابلات - شاشة إظهار كاملة (HMI). - بطاقات نظام التحكم (المعالج , وحدة التغذية , وحدات الدخل/الخرج ) . بالنسبة للمضخات : (محور عدد اثنان , طقم باكات عدد أربعة , طقم بروانة عدد اثنان ) . بالنسبة لمضخات المعايرة الكيميائية : ( طقم صمامات عدد اثنان , طقم موانع عدد أربعة ) 7-3- المخططات وكتب التشغيل : أمور تجب على المتعاقد ( يتعهد بها العارض ) : - تسليم شركة مصفاة حمص ثلاثة نسخ ( باللغة الانكليزية) لجميع كتب معطيات التصميم , مخططات التوضع التفصيلية إضافة الى الوثائق التي تتعلق بأعمال التشغيل والصيانة .لجميع تجهيزات المرجل من مضخات ومراوح ومحركات وصمامات وأجهزة وغيرها . - تقديم مخططات حلقات التحكم , على أن تقدّم البرمجيات المستخدمة في نظام التحكم على CD (ثلاث نسخ ) . بحيث تسمح هذه البرمجيات بالدخول لمكونات النظام وإمكانية التعديل بسهولة . - على العارض تقديم نشرات و كاتالوكات فنية كافية لدراسة العرض المقدم . 7-4- التدريب : - تدريب خارجي : -على العارض تقديم عرض خياري بتدريب /4/ أشخاص في (بلد المنشأ) ولمدة أسبوع, وفق الجدول التالي : الوصف; عدد المتدربين; مدة التدريب. تشغيل وصيانة; 2; أسبوع واحد. أجهزة: التدريب على مكونات وبرمجيات النظام ) software- hard ware ).; 2; أسبوع واحد. وتتحمل شركة مصفاة حمص كافة النفقات (السفر- الإقامة- .......). 2- تدريب داخلي: - لـ/4/أشخاص في الموقع على (تقنية تشغيل المرجل وصيانته في الموقع)ولمدة أسبوع - لـ/3/ أشخاص في الموقع على ( تشغيل واستثمار وصيانة الأجهزة ) ولمدة أسبوع. 7-5- مدة التنفيذ : 365 يوماً 7-6- التزامات الإدارة : - - تتعهد الإدارة بتسليم موقع المرجل الجديد الذي سوف يكون قرب مراجل الطوارئ للمتعاقد. - تتعهد الإدارة بتقديم الكهرباء , الماء ,هواء الأجهزة , و الفيول والغاز ومياه التبريد .... الخ أثناء تشيد المشروع . المرفقات : 1 - المواصفات القياسية السورية للفيول . 2- المواصفات الفنية لغاز الحرق . - الستاندرات والكودات المطلوبة . النهاية | Book of Technical Conditions For Supplying, Installing And Operating Steam Boiler 38kg/cm² Homs Refinery Co. (on-turn Key Basis) Contents : - Scope of Work. - Mechanical Part. - Electrical Part . - Instruments part . - Civil Part . - Water treatment part . - General Requirements . - Attachments . 1- Scope of Work : The project will cover the following : design, supply, erection and operating steam boiler , the project is ( on turn key job basis ) . The project will be delivered to HRC in guaranteed conditions workings . According to the following technical specifications : - Outlet steam pressure : 38 kg/ cm² . -Outlet steam temperature : 450±5 C° . - Outlet steam quantity : 25 t/h at least . - Number of the burners : two burners . 2-Mechanical Part. 2-1- Boiler Data : - Outlet steam pressure : 38 kg/ cm² . -Outlet steam temperature : 450±5 C° . - Outlet steam quantity : 25 t/h at least . Water and fuel specification provided by refinery : -Boiler feed water temperature : ambient temperature ( 5-20 ) C° . -Boiler feed water type : dimi water ( treated ) (water specifications attached) . - Feed water pressure : systematic atmospheric pressure . - Types of used fuels : a- Fuel oil (specifications attached) with systematic atmospheric pressure and temperature ( 70-80 )° C to boiler borders. b- Fuel gas (specifications attached) with pressure ( 3.5-4) kg/cm2. 2-2- Technical Requirements : -The boiler shall be capable of producing steam at rated final pressure , temperature and steam flow when burning any of the specified fuels . - Operational pressure and the temperature of steam should be constant at any boiler's capacity beginning from 60% . - The efficiency should not be less than 91% of nominal load . - The bidder should provide fuel consumption drawings ( fuel- oil / fuel gas ) for boiler . - The bidder should mention the types of metals for all pipes used in the boiler and their physical, chemical and mechanical specifications according to related standards . - the bidder should provide two feed water pump groups with their required accessories for feeding the boiler , one in operation the other is on standby . - The delivered burners must be in accordance with the up to date low NOx type and must be able to burn completely , cleanly and efficiently all the fuels specified above . - A reduction pressure station of 38/14 bar with automatic control should be erected with its accessories . - A special stack for the boiler should be erected independently and it should achieve the operational and environmental conditions. - The contractor should install suitable valves on all pipes, that allow to insulate the boiler from all inlet and outlet pipes . - The contractor should erect galvanized ladders , stairs ,platforms and walkways for complete access to all instruments and equipment easily . - The boiler must be protected by a suitable shelter . -All materials and equipment must be new and not renewed , # - The bidder could pay a visit to H.R.C. in order to be fully aware of the site of erecting the boiler . 2-3- insulation : - All surfaces with temperatures exceeding 60 C° shoud be insulated wherever needed . The boiler, vessels and pipes have to be insulated by any material environmentally accepted and this material have to be protected with aluminum sheets . - Easy removable insulating boxes have to be fitted in all locations that may need to be dismantled for reparation purposes . 3- Electrical Part Electrical Requirements : 1- All electric equipment of the boiler must be suitable for the EX. PROOF acc. to the type of the material which will be used to operate the boiler . 2- The submitted electric equipment of the boiler must be acc. to an international standard : ( NEC- IEC) or their equivalents. 3- Electric used system : 380 / 220 -50 Hz 3 ph +N+PE - 400 Volt - acceptable . 4- All drawings - Catalogs - single line diagram - must be submitted. 5- EX-PROOF - Certificate must be submitted for the motors and the relative equipment. 6- H.R.C will provide the necessary electric power for the boiler operation board . 4- Instrumentation Part 4-1- : Field Instrumentation - include ( local indicators , switches , transmitters,…) for operating parameters ( Pressure , level , temperature , and flow ). - All field instruments should be of modern types , protection degree IP67 , designed and installed in line with current EUROPEAN STANDARDS or their equivalents. - Power supply of all field instruments is 24 VDC. #### 4-2- Automatic Control of Boiler The offered control system should be pragramable logic control (PLC) which consists of the following loops at least : - Combustion control system . - Feed water control loop. - Steam temperature control loop . - Burner management system (BMS) . - local control cabinet for every burner should be installed with protection degree IP55 at least . - control System components should be of modern version for this kind of steam boilers control . - Human Machine Interface (HMI) should be installed . - Possibility for operating and shutdown from site OR HMI . - HMI should have screen for monitoring in real time and archive. And display the alarm and protection states . - PLC modules installed in suitable cabinet with racks and connect with HMI . the contractor should built a suitable room for plc cabinet. Allowing to easy work with cabinet. - The contractor should install all parts for safety operating and shutdown according his design ( relays , lamps ,contactors , horn , …) even they aren't mentioned above . 4-5- The System Accessories : - Portable computer (Labtop) for loading the control software . - Colored laser printer to print the reports . 4-6- Cables : - The bidder should provide cables(Armed, PVC isolation, Copper shield, High temperature resistance) - To lay the cables inside metallic tunnels with tracks according to the boiler environments . - 25% as cables reserve . 5- Civil Part 5-1 Site Information : Site Description :The project will be done in Homs Refinery Co. which is at elevation of about 495 meters above sea level. Soil Information :The contractor has to do all necessary tests on the soil for design purpose. 5-2- Excavation & filling : - The contractor has to execute excavation works ( trenches , electric channels , foundations …..etc) and fill back the excavated areas with suitable soil in well compacted layers. -all electric cables must be laid in concrete channels witch will be filled with sand and must be dyed with red color . 5-3- Drainage And Sewerage System : The bidder should adhere to submit a design for drainage and sewerage system for all the works and this system should be connected with the existing drainage and sewerage system . 5-4- Painting: The bidder has to include in his offer his selection for the painting system for piping , steel structure , mechanical equipment, etc .... 5-5- Earthquake: Degree VII according to( MSK scale or Mercalli) . 5-6- Fire Alarm System : - The contractor should supply and erect fire alarm system and connect it with the general fire alarm system of the refinery . 6- Dimi Water Part 6-1- Specifications of Feed Water - PH = ( 7±1 ) . - Conductivity ( 25° C ( = 0.5 µ S/cm . - Sio2 content = 20 µg/L . - Temperature : Ambient . 6-2- The Internal Chemical Treatment System of Boiler : - The bidder should provide the required chemical protection system for the boiler , in addition to all required equipment such as pumps , tanks and their accessories , and to provide chemical materials usually used for this purpose during one year guarantee period , and to guarantee safe and well operation , and they should be erected on 0.00 m . All above mentioned items should be according to the international standards . 6-3- Samples : - The bidder should provide all necessary sampling equipment and required laboratory apparatuses to make samples analyzing ( spectrophotometer , conductivity , PH)at least . these equipment should be according to international standards . - The bidder should provide the way of analyzing the samples which should be acc. to international standards . 6-4- Chemical Cleaning of the Boiler : - The bidder should offer all the required chemicals ( quantity , quality ) which will be used in the chemical cleaning of the boiler , and the related technical documents . - The bidder should offer the procedure of chemical cleaning the boiler acc. to related international standard , chemical cleaning should be done 7-General Requirements 7-1- General : - The boiler shall be designed , constructed and tested for acceptance in accordance with latest editions of related standards . " a table of required standards is attached ". - The contractor must symbolize all lines and equipment .in addition to marking All measurement parts according to the project drawings. - The contractor must connect his lines with refinery lines( water, fuel ,air , steam ..) - The contractor should supply time schedule for works execution . - Any damage caused by the contractor or his sub-contractor to any part of exciting installation on the HRC such as roads , electric cables ,water , steam pipes ……etc shall be on his responsibility . - The contractor should take the rules of safety in H.R.C into consideration during the execution . - The performance and operation tests will be carried out within a period of one week in order to prove the guarantees . - The contractor must provide Test certificate for all equipment in English. Bidder should provide detailed price list for all works (Supply and Installation and operating ) in his financial offer . 7-2- Spare Parts : - The bidder should submit spare parts lists ,for five years operation, un priced one within the technical offer and another priced one within the financial offer , H.R.C. keeps the right to choose suitable items during the technical study . - spare parts lists should include at least the followings : instrumentation part - The main components necessary for burner starting ( flame detector , ignition electrode,… etc) - 10 % of cables' length. - HMI unit . - PLC modules ( CPU, PS , I/O ,..) PUMPS : ( 2 shift , sleeve : 4 sets , impeller : 2sets ) . CHEMICAL PUMPS : (valves: 2sets , seals : 4sets ) 7-3- Manuals And Drawings : ( The bidder adhere )The contractor will have to: - hand over to HRC three copies ( in English language ) of all the design data books , lay out detailed drawings as well as all the documentations relative to the operation and maintenance work . for all boiler equipments ( pumps, air fan , motors , valves , instruments ,….etc) . - Submit all control loops diagrams , all used programs on CD (3 copies ) .with the possibility of modify easily. - The bidder should submit catalogs and information sheets to study the offer . 7-4- Training : 1- External training -The bidder must submit an optional offer to train /4/ persons in the country of origin ,. ) for one week according the following schedule : Description; No. of trainees; Duration. Operation and maintenance; 2; One week. Instrumentation : training on the programs and components of system(soft ware – hardware .; 2; One week. - HRC is responsible for all costs (travel, lodging…) 2- Internal Training : - For /4/ persons of HRC in the site to attend technical seminar ( on the technology and operation of boiler ) for one week . - For /3/ persons in site , on (operation , investment and maintenance of instruments ) for one week . 7-5- Execution period : 365 days . 7-6- The Administration's Obligations : - The administration will deliver the site of new boiler which will be near the emergency boilers to the contractor . - The administration adhere to submit electricity , water , instrument air , fuel oil , fuel gas and cooling water ……etc .during erecting the project 7-7- Attachments : 1- Syrian Specification Standard of fuel . 2- Technical specifications of fuel gas . - Required standards and codes . END |
| --- | --- |

مواصفات مياه التغذية  ( الديمي )                                             Demi - WAter

-   pH                                                                                           7   ± 1

-   SiO2                         ppm    aa       SiO2                            0.02

-    Conductivity   at      25  C                                    0.5 µ s / cm

المواصفات الفنية للغاز الطبيعي

( Natual) OMAR  GAS FILED

CH4                                                    75

C2H6                                                   10

5	  		C3H8

0.25                                  i-C4H10

0.4                                                  n-C4H10

0.02                              	i-C5H12

0.00                               n-C5H12

9.50                                      CO2

0.00                                        H2

0.00	H2S

Density               =      0.9 kg/m3

10600 Kcal/kg   =    Caloric value

مرفق رقم واحد           Attachment no . 1       م .ق . س.  155

الجدول (1) الخصائص الفيزيائية والكيميائية :

| الخصائص | المتطلبات | Specifications | طرائق الفحص والاختبار |
| --- | --- | --- | --- |
| الكثافة عند الدرجة ( 15 ) °س ( غ/سم³ ) حدا أعلى | 0.995 | Specific gravity at (15°C ) g/cm² at most | ASTM - D 1298 |
| درجة الوميض ( وعاء مفتوح ) °س حدا أدنى | 100 | Flash point ( open ) min 0 | ASTM - D92 |
| اللزوجة بدرجة ( 210 ) ف ( سنتي ستوك ) حدا أعلى | 40 | Viscosity (210 F ) centistokes | ASTM - D445 |
| نسبة الكبريت الكلي ( % وزنا ) حدا أعلى | 4.5 | Sulfur( % weight ) max | ASTM - D1552 |
| نسبة الرماد ( % وزنا ) حدا أعلى | 0.10 | Ash ( % weight ) max | ASTM - D482 |
| درجة الانصباب ( % وزنا ) حدا أعلى | + 24 | Pour Point ( % weight) max | ASTM - D97 |
| القيمة الحرارية ( صافي ) كيلو كلوري لكل كغ , حدا أدنى | 9200 | Caloric Value ( pure ) k cal / Kg , min. | ASTM - 240 |
| محتوى الماء والرواسب ( % وزنا ) حدا أعلى | 0.50 | Water by distillation ( %) weight max . | ASTM - D 96 |
| نسبة الاسفلتينات حدا أعلى | 8 | Al Sphattenes , max | UOP-614 OR ASTM -6560 |
| محتوى الماء بالتقطير ( % ) حجما حدا أعلى | 0.5 | Water by distillation ( %) volume max . | ASTM - D-95 |
| نسبة الفاناديوم ( جزء بالمليون ) حدا أعلى | 125 | Vanadium ( part of million ) max | UOP-391 OR ASTM -5863 |
| نسبة الصوديوم ( جزء بالمليون ) حدا أعلى | 40 | Sodium ( part of million ) max | UOP-391 OR ASTM -5863 |
| الرواسب الكلية ( % وزنا ) حدا أعلى | 0.15 | Total sediments( % weight) max | IP -375 or ASTM -D-4870 |

4  -   -       الاعتيان

يتم الاعتيان بواسطة المواصفتين السوريتين التاليتين :

4/1   المواصفة رقم /506  / الخاصة ب : المنتوجات النفطية - الفحوم الهيدروجينية السائلة - الاعتيان اليدوي .

4/2   المواصفة رقم / 507 / الخاصة ب : المنتوجات النفطية - الفحوم الهيدروجينية السائلة - الاعتيان الآلي من خط الأنابيب .

اللجنة الفنيــــــــــــــــــــــة

ك.علي عكاري            م. عبد الرحمن الهميش             م.عناد رومية         م . ابراهيم وسوف

م.أحمد الحسن            م. هالة الشاويش             م. وديع السبعة                  رئيس اللجنة

م. نزار الحاج حسين

المدير العام / بالتكليف

المهندس / علي حسن طراف